WARNING

Analog output lines must not be connected to any kind of voltage or current source, serious damage will result.

(OPTIONAL) STROBE  LIGHT

# Text boxes

Cable Color Code

White - S     Signal

Black - G     Ground

Red -  +V     7.5 VDC

Notes:

1.  Power Cord - Provided w/ wall plug connector and 8 Ft. 3 conductor wire.

2.  Audible and Visual Alarm (Optional) factory wired.  Remote Audible and Visual Alarms

must be 120VAC and connected to terminal Strip on Lower Circuit Board.

3.  Sensor Cable between Haloguard( Controller and CMOS Sensor - Maximum Length 300FT. Use

3 conductor 18 or 20ga. w/ foil shield.

4.  Analog Outputs (Optional) are either 0 - 5VDC, 0 - 10VDC, or 4 - 20mA.

Lower Circuit Board

ANALOG OUTPUTS

TO BAS OR OTHER

+V S G

Haloguard(  Controller

+  A  +  S

See Chart for Connection

+

-

(Optional)

BATTERY

BACK-UP

Plug in Molex Connector

1

3

2

4

6

5

7

9

8

10

12

11

2

3

4

5

6

7

8

9

10

11

12

ALARM

1

FAULT

OFFSCALE

ALARM

2

Green

Line Cord

115 VAC 50/60Hz.

AC HOT

ACCOMMON

GROUND

G

N

L

White

Black

8’ Cable w/ DIN Plug in Connector

See notes below for cable extension.

(OPTIONAL)

AUDIBLE ALARM